## Tune-Up Worksheet
Overarching Guidelines
*If a building does not contain a certain element or system associated with an Assessment Element, the Qualified Tune-Up Specialist should note this in the Inspection Finding column, and no corrective action is required.
* For any actions where a building owner can clearly demonstrate a reasoning for specific operations (e.g., meeting a specific use case, addressing a health issue, etc.), the owner may be exempt from completing the corrective action. A valid reasoning does not include personal preference. The Tune-Up Specialist must sign-off on the reasoning and include it in the Description of Extenuating Circumstances column
* The Qualified Tune-up Specialist must detail the outcomes of each assessment in the "Inspection Finding" column, state whether or not there is a deficiency, and provide brief detail as to why it is a deficiency
*If the Qualified Tune-up Specialist observes a deficiency, the Specialist must describe the action(s) they recommend to remedy it in the Corrective Action Description column
*Where a sampling is permitted, the Qualified Tune-up Specialist can conduct a randomized inspection of at least 15% of that element, unless otherwise specificed in the Assessment Overview column. Within the "Sampling Approach" column, the Tune-Up Specialist must note the number of elements included in the random inspection, the total number of elements in the building (can be estimated), and the number of floors (as a % of total) on which an element was inspected.
*If over 50% of sampled elements demonstrate need for corrective actions, the Qualified Tune-Up Specialist should provide a recommendation to the building owner in the Corrective Action Description column about if (and how) to review and/or correct potential issues among the broader set of the elements throuhgout the building. Corrective action on elements outside the sampling range is voluntary. The building owners should provide to the Qualified Tune-up Specialist a description of further steps beyond fixing the sampled elements, if any, the building will take. The Tune-up Specialist should note this within the End Condition column and describe what, if anything, was completed during the final review.
*For assessment elements related to system maintenance & repairs, building owners and tune-up specialists should proceed according to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition)
Action # | Assessment element | Inspection Overview | Corrective Action | Required / Voluntary (to remove in final worksheet; color code) | Inspection Finding | Deficiency? (Y/N) | Sampling Approach (if applicable) | Corrective Action Description (if applicable) | End Condition/Current Condition (If deficiency observed, state end condition after implementation of corrective action. Otherwise, state current condition.) | Description of Extenuating Circumstances (If applicable)
Section 1) Building System Maintenance & Repairs (clean and adequately maintained according to ANSI/ASHRAE/ACCA Standard 180-2012, or current edition)
1.1 | Grilles and Coils | Inspect a sampling of grilles and coils. Assessment may be based on a random sampling of at least 15% of each element. | Clean and maintain where impacting system performance. | Required
1.2 | Filters | Inspect a sampling of filters to determine if clean and regularly maintained. Assessment may be based on a random sampling. | Clean or replace filters where impacting system performance | Required
1.3 | Strainers | Inspect sampling of strainers to determine if clean and regularly maintained. | Show evidence of recommended cleaning/blowdown. Clean or replace strainer screen where impacting system performance | Required
1.4 | Motors and Belts | Inspect sampling of motors and belts. | Clean lubricate, adjust, replace or repair where impacting system performance and where doing so is a standard or regular maintenance action | Required
1.5 | Filters, Strainers, Motors, Belts | If scope of work to rectify deficiencies found in 1.2, 1.3, and 1.4 is more than standard or regular maintenance, recommend repairs. | Implement repairs | Voluntary
1.6 | Dampers and valves | Inspect sampling of dampers and valves for proper functionality, including opening and closing fully. | Repair as needed where impacting system performance | Required
1.7 | Variable frequency drive (VFD) | Review the modes for any VFDs. | Place VFDs in "Auto" mode. Adjust BAS or controls as appropriate for system performance | Required
1.8 | Service Life of Major Equipment | Identify equipment approaching the end of its service life, per ASHRAE Service Life Database. Recommend replacement plan and schedule | Implement replacement plan and schedule. | Voluntary
1.9 | Visible Ducts and pipes | Inspect ducts and pipes that are visible and make recommendations for where new insulation or repair to existing insulation would enhance system performance. This should inlcude steam pipes. Provide indicative pricing for insulation and/or repairs in these locations. | Implement recommendations for insulating or repairing pipes and/or ducts. | Voluntary
1.10 | Steam Traps | Inspect the main steam traps to determine if they have failed. | Replace failed steam traps, if any. | Voluntary
Section 2) HVAC Operations and Controls
2.1 | Occupancy Scheduling, Temperature Setbacks and Supply Fan Cycling | Review HVAC equipment schedules (Including daily, weekly, seasonal, day/night, occupied/unoccupied hours). Review HVAC set points (including space temperatures, supply air temperatures, CO2, economizer changeover temperatures, supply fan cycling and static pressure). | Set schedules and setpoints as appropriate to support building use, occupancy patterns, and occupant needs. | Required
2.2 | Temperature and Static Pressure Resets: Hot Water, Chilled Water, Distribution Air Temperature | Review reset schedules (including supply air temperature, supply air pressure, boiler and chiller water temperature, lockouts with outside air temperature, loop differential pressure). | Establish or adjust schedules as appropriate to support efficient operations. | Required
2.3 | Economizer Mode, Demand Controlled Ventilation, and/or Minimum Outside Air Controls | Review minimum outside air controls, including demand controlled ventilation and OA controls for economizer mode, to verify ventilation rates do not vary significantly from rates specified in ASHRAE 62.1 Standards for current facility type | Correct and repair equipment in areas where ventilation rates vary significantly from ASHRAE 62.1 Standards and are inappropriate for current facility requirements (e.g. no outside air supply or 100% outside air supply, etc.). | Required
2.4 | Optimal Start/Stop | Review optimal start/stop capabilities | Establish or confirm optimal start/stop capabilities as appropriate to support the building use and occupant needs | Required
2.5 | Simultaneous Heating and Cooling | Review HVAC controls for unintended or inappropriate instances of simultaneous heating and cooling. | Adjust HVAC controls to reduce or eliminate any unintended or inappropriate simultaneous heating and cooling | Required
2.6 | Major Equipment Sensors | Verify that HVAC sensors are functioning, calibrated, and in appropriate locations. Sensors may include, but are not limited to, zone temperature; outside air/return-air temperature; mixed air/discharge air temperature; pressure; occupancy; humidity. The assessment can include a sampling of sensors and must group like sensors (e.g. discharge, space, etc.) to meet the 15% sampling floor. | Repair, adjust, move in close proximity or recalibrate as appropriate. | Required
2.7 | HVAC Controls | Verify HVAC controls are functioning as intended for building operation. | Adjust control sequences as appropriate for current facility requirements | Required
2.8 | Exhaust fans | Inspect exhaust fans to determine if they are functioning and if controls (e.g. schedule or sensor) are properly calibrated | If deficiency found, adjust schedule, fix sensor, and/or repair fan. | Required
2.9 | Central Plant Operations | If a Central Heating and/or Cooling Plant exists, review the operations. Review HVAC set points (boiler supply and return temperatures, chilled water supply and return temperatures, condenser water supply and return temperatures, water or steam system pressures, and equipment sequencing). | Set schedules (including seasonal shutdowns) and setpoints as appropriate to support building use, occupancy patterns and occupant needs. | Required
2.10 | Air Balancing Issues | Note any indications of significant air-balancing issues (e.g. wind-tunnel effect). | Recommend rebalancing of HVAC air and water systems where significant efficiency or comfort improvements can be achieved | Voluntary
2.11 | Dominant Zones | Identify zones that are dominating multi-zone system operations, and that cause inefficiencies and/or comfort issues. Recommend solutions to isolate these zones. | Implement recommendations | Voluntary
2.12 | Cooling Tower Fan Operation | If cooling tower is two cell or greater, review fan operation. Determine whether fans are running in parallel or in sequence, and recommend running in parallel unless cooling tower configuration requires sequence operation. | Implement recommendations | Voluntary
2.13 | Variable frequency drive (VFD) applications | Identify areas that could benefit from variable frequency drives; identify pump and fan motors that are prime candidates for VFD upgrades |  | Voluntary
Section 3) Lighting System Assessment
3.1 | Lighting Control Schedules and Sequences | Review lighting controls, schedules and sequences (including daily, weekly, seasonal, day/night, occupied/unoccupied hours). | Set schedules and controls so they appropriately match building use, occupancy patterns and occupant needs, and limit wasted energy to the extent possible. | Required
3.2 | Light Levels | Identify areas where lighting levels are significantly higher than appropriate for the space use and occupancy needs. Recommend dimming, delamping or other options to improve lighting to support building use and occupant needs. | Implement options recommended to adjust for appropriate lighting levels | Voluntary
3.3 | Inefficient Lighting and Sensors | Identify low-cost lighting energy conservation measures that would enhance system performance (specifically inefficient incandescent, fluorescent, or metal halide lighting; and opportunities for lighting controls). Provide indicative pricing for the proposed solutions. | Implement low-cost light energy conservations measures | Voluntary
3.4 | Functional Lighting Sensors | Where installed, verify lighting sensors are working as designed | Repair any malfunctioning lighting sensors | Voluntary
Section 4) Domestic Hot Water and Water Usage
4.1 | Domestic Hot Water | Review domestic hot water setpoints to determine if the current setpoints are appropriate for the buildings use cases | Lower setpoints to the minimum temperature possible that will not adversely affect operations | Required
4.2 | Circulation pumps | Review circulation pumps to ensure they function and set according to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition) | If not functioning, fix the circulation pumps. If not set to meet to ANSI/ASHRAE/ACCA Standard 180-2012 (or current edition), adjust as appropriate. | Required
4.3 | Plumbing Fixtures | Either: 1) Inspect 10% of plumbing fixtures for leaks or other maintenance needs. Expand inspection to 20% if deficiencies found in 50% or more of a specific type of fixture OR 2) Review a comprehensive maintenance report of fixtures kept by on-site staff to determine any potential maintenance needs (must show at least quarterly inspection) | Conduct standard or regular maintenance actions on fixtures requiring repair. | Required
4.3.1 | Plumbing Fixtures | If scope of work to rectify deficiencies found in 4.3 is more than standard maintenance (e.g., replacement of entire fixtures) recommend repairs. | Implement recommended repairs | Voluntary
4.4 | Cooling Tower | Evaluate cooling towers for water leaks and excess water consumption. Also verify that cooling tower conductivity meter used to control blow down is calibrated and functioning properly | Repair any leaks and address excess water consumption. Calibrate meter appropriately | Required
4.4.1 | Cooling Tower | If evaluation returns any deficiencies that fall beyond normal maintenance, recommend repairs | Implement repairs | Voluntary
4.5 | Water Usage setpoints and controls | Review makeup water controls for temperature control (including cooling tower makeup water) and irrigation systems. | Adjust setpoints and controls as necessary to improve efficiency. | Required
4.6 | Water Features | Review water feature schedules to ensure they shut-down during night-time or unoccupied periods, where appropriate | Implement scheduling changes | Required
4.7 | Water flow fixtures | Check for use of low flow fixtures and aerators. Assessment may be based on a random sampling of at least 5% of each type of fixture. | Install low flow fixtures and/or aerators, as appropriate. | Voluntary
Section 5) Building Envelope
5.1 | Roof condition | Check for roof penetrations, gaps, and/or damage that could allow for the entry of air or water (such as at dampers or top of elevator shaft) | Repair issues, as appropriate | Voluntary
5.2 | Roof and Wall Insulation | Identify and recommend insulation in areas impacting system performance that are outside of a standard or regular maintenance action. Recommend Cool Roof coating where appropriate. | Implement recommendations | Voluntary
5.3 | Windows and doors | Inspect age and condition of windows. Inspect both windows and doors for seals, weatherstripping, etc. Identify and recommend repairs impacting system performance that are outside of a standard or regular maintenance action. Inspection only required for a representative sample of doors and windows. | Implement recommendations | Voluntary

## Data Req.
Building Data Requirements
Building Info |  | Comments
Name
Address
OPA #
Portfolio Manager ID#
Owner Info
Name
Company
Mailing Address
Contact Information (email, phone)
Building Manger/Tune-up contact Info (Can be "Same as above")
Name
Title
Company
Mailing Address
Contact Information (email, phone)
Building Characteristics
Sq. Ft.
Building Age
# of floors
Basements/sub-basements
# EV charging stations
Occupancy (as % of total)
Fuel sources used (list all)
Define Major Space Uses (up to 5 or all spaces over 20,000 sqft)
Office, Retail, Parking, etc….
Define Major Systems supporting each space
Major Systems (Centralized or Decentralized)
Air Handling, Venitilation and Distribution Systems
Air Conditioning, Central Chiller and Cooling Tower Systems
Boilers and Heating Systems
Domestic Hot Water Heating Systems
Lighting Systems
Misc or Other Pumping Systems
Misc or Other Building Electrical Systems
Occupancy details for spaces
General Schedules
Setbacks
Setpoints
Define Type of System and Major Equipment
| List of Major Systems | Age | System Size Threshold | Unit | System Size Threshold (Optional for listing different unit) | Unit | Comments
| Hot Water Heating Plant |  |  | MBH
| Steam Heating Plant |  |  | MBH
District Steam
District Cooling
| Chilled Water Plant |  |  | Tons
| Humidification System |  |  | MBH
Energy Recovery Loops
Ventilation Systems
| Domestic Hot Water Heating |  |  | MBH
Building Automation System
On-site Power Generation
Energy Storage Systems
| Major Equipment (Centralized) | Age | System Size Threshold | Unit | System Size Threshold (Optional for listing different unit) | Unit
| Boilers |  |  | MBH
| AHUs (Single Zone, Multizone, VAV, etc) |  |  | CFM
| RTUs served in part from Central Plant (Single Zone, Multizone, VAV, etc) |  |  | CFM
| FCUs |  |  | CFM
| Chillers (Air and Water Cooled) |  |  | Tons
| Cooling Towers |  |  | Tons
| Centralized Heatpumps (Air and Watersource including VRF) |  |  | Tons/ BTU
| Heatexchanger (Heating or Cooling) |  |  | Tons/ BTU
Major Equipment (Decentralized) use sampling approach of at least 15%
Window Units
Unit Heaters
Packaged RTUs (Single Zone, Multizone, VAV, etc)
Makeup Air Unit
Decentralized Heatpumps and Split systems (Airsource)
PTAC or PTHP (Packaged Terminal Units)
Energy and Water Use Data
Include energy benchmarking data. Review the data for any errors. If necessary, correct any errors and have building resubmit reports.
Review energy bills (monthly for past year, at least) for any abnormalities that could indicate poor or inappropriate functioning of systems and/or equirpment. If found, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.
Review water bills (monthly for past year, at least) for any abnormalities that could indicate poor or inappropriate functioning of systems and/or equirpment. If found, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.
Include carbon footprint/carbon emissions data (voluntary)
Tenant-related Information
How is water metered in the building: Is it master metered or do tenants have separate meters?
Do tenants pay for their own energy use? (Yes or no)
Does Building Owner/Manager run a tenant engagement program on energy efficiency? If yes, provide a brief description of this program
Maitenance Review (Voluntary)
Review recent (e.g. last quarter) of tenant complaints regarding building systems and maitenance records. If complaints point to poor or inappropriate functioning of systems and/or equirpments, include a summary of potential issues and further elaborate if specific tune-up items may be required to fix these issues.